## sample-records
Record_type | Record_id | Date | A sset_id | technician_id | key_metric_metric | key_metric_imperial | unit_metric | unit_imperial | summary | notes
ASSET | PLT-CHL-001 | 2018-03-15 | PLT-CHL-001 | N/A | 1758 | 500 | kW | ton | Water-cooled centrifugal chiller (R-134a) | # EXAMPLE â€” anon
ASSET | PLT-CHL-002 | 2020-07-22 | PLT-CHL-002 | N/A | 1055 | 300 | kW | ton | Water-cooled screw chiller (R-514A) | # EXAMPLE â€” anon
ASSET | PLT-AHU-014 | 2019-11-05 | PLT-AHU-014 | N/A | 90 | 25 | kW | ton | Built-up AHU West Wing | # EXAMPLE â€” anon
ASSET | PLT-CT-001 | 2017-06-12 | PLT-CT-001 | N/A | 3516 | 1000 | kW | ton | Counterflow cooling tower cell 1 | # EXAMPLE â€” anon
ASSET | PLT-PMP-CHS-001 | 2018-03-15 | PLT-PMP-CHS-001 | N/A | 15 | 5 | kW | ton | CHW primary pump 1 | # EXAMPLE â€” anon
SERVICE | CHL-SVC-2025-014 | 2025-01-14 | PLT-CHL-001 | T-1001 | 1.4 | 2.5 | degC | degF | Annual chiller service â€” condenser approach 1.4 degC | # EXAMPLE â€” readings illustrative only
SERVICE | CHL-SVC-2025-028 | 2025-03-02 | PLT-CHL-002 | T-1002 | 0.9 | 1.6 | degC | degF | Screw chiller annual service â€” evaporator approach 0.9 degC | # EXAMPLE â€” readings illustrative only
INSPECTION | AHU-2025-1014 | 2025-01-14 | PLT-AHU-014 | T-1001 | 13.5 | 56.3 | degC | degF | Monthly AHU inspection â€” SAT 13.5 degC vs setpoint 13.0 degC | # EXAMPLE â€” anon
INSPECTION | CT-2025-1014 | 2025-01-14 | PLT-CT-001 | T-1001 | 4 | 7.2 | degC | degF | Cooling tower inspection â€” approach to WBT 4.0 degC | # EXAMPLE â€” anon
INSPECTION | PMP-2025-014 | 2025-01-14 | PLT-PMP-CHS-001 | T-1001 | 1.6 | 0.063 | mm/s | in/s | Pump vibration inspection â€” DE vibration 1.6 mm/s within zone B | # EXAMPLE â€” anon
FILTER | FLT-2025-014 | 2025-01-14 | PLT-AHU-014 | T-1001 | 90 | 0.36 | Pa | inH2O | Filter replacement â€” final DP after replacement 90 Pa | # EXAMPLE â€” anon
REFRIG | RSV-2025-014 | 2025-01-14 | PLT-CHL-001 | T-1001 | 2.5 | 5.51 | kg | lb | R-134a topup after filter change â€” 2.5 kg added | # EXAMPLE â€” anon
REFRIG | RSV-2025-028 | 2025-03-02 | PLT-CHL-002 | T-1002 | 168 | 370 | kg | lb | R-514A full recovery-recharge â€” 168 kg recovered | # EXAMPLE â€” anon
FAULT | FLT-2025-014 | 2025-01-14 | PLT-CHL-001 | BMS | 2 | 2 | h | h | High condenser pressure â€” 2.0h downtime | # EXAMPLE â€” anon
FAULT | FLT-2025-028 | 2025-02-03 | PLT-AHU-014 | Operator | 1.5 | 1.5 | h | h | Supply temp sensor drift â€” 1.5h downtime | # EXAMPLE â€” anon
FAULT | FLT-2025-035 | 2025-02-19 | PLT-PMP-CHS-001 | BMS | 72 | 72 | h | h | DE bearing wear â€” 72h downtime | # EXAMPLE â€” anon
READING | RDG-2025-0141 | 2025-01-14T08:00:00 | PLT-CHL-001 | BMS | 7 | 44.6 | degC | degF | CHW supply temp â€” 7.0 degC | # EXAMPLE â€” anon
READING | RDG-2025-0150 | 2025-01-14T08:00:00 | PLT-AHU-014 | BMS | 13.5 | 56.3 | degC | degF | AHU supply air temp â€” 13.5 degC | # EXAMPLE â€” anon
READING | RDG-2025-0155 | 2025-01-14T08:00:00 | PLT-CT-001 | BMS | 32 | 89.6 | degC | degF | CW hot water inlet â€” 32.0 degC | # EXAMPLE â€” anon
READING | RDG-2025-0158 | 2025-01-14T08:00:00 | PLT-PMP-CHS-001 | BMS | 14.5 | 14.5 | A | A | Pump motor amps â€” 14.5 A vs 19.3 FLA | # EXAMPLE â€” anon
PM | PM-CHL-001-028 | 2025-01-05 | PLT-CHL-001 | Certified technician | 1 | 1 | event | event | Monthly F-Gas refrigerant leak check â€” no leak found | # EXAMPLE â€” anon
PM | PM-CHL-001-180 | 2025-01-14 | PLT-CHL-001 | OEM service provider | 1 | 1 | event | event | Annual chiller service completed â€” oil sample sent for analysis | # EXAMPLE â€” anon
PM | PM-CT-001-001 | 2025-01-14 | PLT-CT-001 | Operator | 1 | 1 | event | event | Daily cooling tower water test â€” pH 7.8 conductivity 1800 uS/cm | # EXAMPLE â€” anon